SECTION 3 - SCOPE OF WORK/SPECIFICATIONS

GENERAL DESCRIPTION

The goal of [Busytown] is to obtain bids for Magnesium Hydroxide slurry. The intent is to enter into an agreement (also referred to herein as “Contract" or “Agreement") for the delivery of Magnesium Hydroxide slurry to preselected locations within the [Busytown]’s collection system and wastewater treatment plant(s) for Hydrogen Sulfide and corrosion control. The Contractor’s price shall include the delivery, offloading and all other associated costs. [Busytown] currently has [Fill in number] magnesium hydroxide locations in its service area.  The Contract will require the delivery of Magnesium Hydroxide slurry to these existing locations and also any future locations at the Contract’s agreed upon price per gallon.

DELIVERY:

The delivery shall be made FOB Destination. Contractor shall make “normal” deliveries within three (3) calendar (i.e., not "working" days) days after receipt of order and must make "emergency" deliveries within 24 hours. An emergency delivery is defined as a delivery which is necessary in order to prevent [Busytown]  from running out of Magnesium Hydroxide in less than 36 hours. [Busytown]  shall endeavor to minimize the number of "emergency" deliveries.

Contractor shall be responsible for any spills resulting from the failure of its or its subcontractor's delivery equipment or from failure of attendant delivery personnel in the proper performance of their duties. Proper performance shall require attendant delivery personnel's constant inspection and observation of unloading operations and knowledgeable response to problems or emergencies, which would most commonly be expected to occur. [Busytown]  reserves the right to refuse any deliveries made with equipment that is poorly maintained and/or leaking. Failure to follow any safety protocols, proper safety equipment usages or comply with any other safety system could result in rejection of the load and could result in termination of the Contractor's supply agreement.

The tanks or trailers shall be clean and free of residue that may contaminate the Contractor's product or impede the unloading process. It is the Contractor's responsibility to verify the cleanliness of the transporting equipment before loading. All appurtenant valves, pumps, and discharge hoses used for the delivery of chemicals shall be supplied by the Contractor and shall be clean and free from contaminating material. [Busytown]  may reject a load if the equipment is not properly cleaned. The Contractor shall furnish [Busytown]  an approved, leak-free connection device between the trailer and [Busytown] 's intake receptacle at each delivery location. The Contractor shall observe the entire filling operation at each delivery site and shall immediately report any spills caused during the filling operations. The Contractor shall take immediate and appropriate actions to clean up any spilled chemical. If the spill is not cleaned up, the cost of such service will be charged to the Contractor and deducted from the amount due to the Contractor. If [Busytown]'s unloading equipment such as piping, valves and/or valves alarms should fail and the spill is not the fault of the Contractor or its subcontractor, the Contractor shall be relieved of cleanup of the spill. Because of security and safety concerns, all delivery vehicle drivers shall be U.S. citizens and have a proper commercial driver's license with a Hazardous Material endorsement. Contractor’s drivers shall display their drivers’ license whenever challenged by [Busytown]  personnel during the delivery.

The following is a list of Current Delivery Locations:

| Name of Location | Address | Size of Tank(s) | Estimated Usage |
| --- | --- | --- | --- |

CONTRACTOR RESPONSIBILITIES

The Contractor and its subcontractors shall:

- Comply with an applicable Federal, State1 and local regulations and laws.

- Comply with [Busytown]'s Environmental Management Systems (EMS) program and all applicable regulations and contract requirements, including [Busytown]'s Environmental Policy Statement.  Contractor must notify their employees and subcontractors about the EMS program and the requirements. Contractor, including its site supervisor and subcontractor, must attend a 30-minute briefing on EMS after a purchaser order (PO) is issued.

It is understood that Contractor activities may accidentally cause environmental harm. Contractor is responsible for notifying [Busytown]  site liaison team (to be designated at time of award) if an incident or accident occurs. For a true emergency, Contractor personnel shall also call 911. Strict adherence to this Specifications is required. There is no allowance for experimentation. Continued contracts and privileges are based on conformance with requirements and may be reviewed in cases of nonconformance.  In-house testing of the chemical performance will be conducted as necessary to ensure compliance.

QUALITY OF MATERIAL

The Magnesium Hydroxide product shall meet the following specifications (the “Product”).  Any bid not meeting these specifications will not qualify and will not be considered.  Additionally, the Magnesium Hydroxide Product manufacturer shall be certified to meet ANSI/NSF Standard 60 and be ISO 9001 certified to confirm it is a quality product.

| Parameters | [Busytown]’s Specifications |  |
| --- | --- | --- |
|  | Maximum | Minimum |
| Physical Properties of Slurry |  |  |
| Density (lbs./gallon) | 12.5 | 13.0 |
| % Solids, Weight Percent | 59 | 63 |
| Viscosity, cps | 100 | 300 |
| Mg(OH)2 contained lb/gallon (Calculated) | 7.0 | 8.0 |
| Timed Liquids/Solids Settleometer Test (48 hrs.) | 250 ml | 240 ml |
| Dry Solids Basis |  |  |
| Mg(OH)2, Weight Percent | 98.5% | 99.0% |
| Calcium as CaO, Weight Percent | None | 0.80% |
| Silicon as SiO2, Weight Percent | None | 0.35% |
| Iron as Fe2O3, Weight Percent | None | 0.21% |
| Median Particle Size, Micron | 1 | 5 |
| Specific Surface Area, m2/g | 10 | 14 |
| % Passing 325 Mesh Sieve | 99 | 100 |
| Lbs. Alkalinity/Gallon as CaCO3 (Calculated) | 13 | 14 |
| NaOH Equivalent to Alkalinity | 1 lb Equivalent to 0.73 lb Mg(OH)2 |  |
| Na2CO3 Equivalent | 1 lb Equivalent to 0.55 lb Mg(OH)2 |  |

TESTING OF MATERIAL

[Busytown]  reserves the right to request or take samples of the supplied chemical for testing prior to the bid award and anytime during the term of the Contract to ensure the product is meeting specifications.

PAYMENT:

Payment will be based on the gallons of the product delivered to each site. All invoices must include beginning and ending tank levels, gallons delivered, cost per gallon, delivery location, invoice number and [Busytown]'s purchase order number.

TYPE OF CONTRACT

[Busytown] anticipates the award of a firm-fixed price contract to a single bidder as a result from this solicitation.

CONTRACT TERM

The performance period (''Term") of the resultant contract will be as follows: Three-Years Initial Term starting approximately [Fill in Date].  Contract shall have two (2) 1-year extensions.

DOCUMENT(S) TO BE SUBMITTED WITH THE BID

The instruction provided in this section serves as a courtesy to the Bidder in preparing its bid submission. It is the bidder's responsibility to completely familiarize itself with the solicitation and its requirements, and to ensure that all required documentation is submitted, even if it not listed below.  The Bidder shall submit/respond with the following technical documentation:

- Safety Data Sheet (SDS) for the Product.

- Manufacturer’s Product Data showing Bidder’s Product meets [Busytown]’s Specifications.

- Third Party Laboratory analysis of Bidder’s Product done in the last three (3) months showing Bidder’s Product meets [Busytown]’s Specifications for Mg(OH)2 weight percent (%), weight percent (%) solids, viscosity, sieve analysis, calcium weight percent (%) as calcium carbonate, silicon weight percent (%) as SiO2, and iron weight percent as Fe2O3.

- ANSI/NSF Standard 60 Certification documentation for the Product manufacturer.

- ISO 9001 Certification for the Product Manufacturer.

- List of any Subcontractors (i.e., for Product Deliveries)